AHCO Life Safety Code Survey Checklist

CODE YEAR – 2012, NFPA 99 & 101 – Final Rule Effective Date: July 5, 2016

Name of Facility: _________________________________________________  Date:  ______________

Provider Number: ___________________

Required Policies and Procedures (Established by the Facility) and Maintenance Logs.

These items should be ready for review during the inspection

	1. Evacuation and Relocation Plan: There is a written plan for the protection of all patients and for their evacuation in the event of an emergency. Employees are periodically instructed and kept informed with their duties under the plan, and a copy of the plan is readily available with telephone operator or with security. The plan addresses the basic response required of staff per 20/21.7.2.1.2 and provides for all of the fire safety plan components per 20/21.7.2.2. 20.7.1.1 through 20.7.1.3, 20.7.1.8 through 20.7.2.3.3 21.7.1.1 through 20.7.1.3, 21.7.1.8 through 20.7.2.3.3. (K711)

	The basic response required of staff shall include the following (NFPA 101, 18.7.2.1.2, 19.7.2.1.2)

- Removal of all occupants directly involved with the fire emergency.

- Transmission of an appropriate fire Alarm signal to warn other building occupants and summon staff.

- Confinement of the effects of the fire by closing doors to isolate the fire area.

- Relocation (Evacuation) of patients as detained in the health care occupancy’s fire safety plan.

	2. Fire Drills:

	Fire drills include the transmission of a fire alarm signal and simulation of emergency fire conditions.

	Fire drills are held at unexpected times under varying conditions, at least quarterly on each shift.

	The staff is familiar with procedures and is aware that drills are part of established routine.

	Responsibility for planning and conducting drills is assigned only to competent persons who are qualified to exercise leadership. 20.7.1.4 through 20.7.14.7 (K712)

	3.* Emergency Preparedness Plan and Drills: (Note: Ch. 12, NFPA 99, not adopted. CMS has developed separate requirements for emergency preparedness.)(K700)(Federal Register, 81 FR, 63859)

	Establish and maintain an emergency preparedness plan, reviewed annually. See appendix for four core elements.

	Provide a written report on mock disaster drill annually.

	Ambulatory Health Care Occupancies, AHCO (ASCs), must document that they have made efforts to communicate with their state and local emergency preparedness officials to inquire about potential coordination.

	4. Fire Alarm System – Testing and Maintenance: A fire alarm system is tested and maintained in accordance with an approved program complying with the requirements of NFPA 70, National Electric Code, and NFPA 72, National Fire Alarm and Signaling Code. Records of system acceptance, maintenance and testing are readily available. 9.6.1.3, 9.6.1.5 (K345).

	Date of Last Inspection 							(annual)

	Who provided system test

	5. (If) Sprinkler System – Maintenance and Testing: Automatic sprinkler and standpipe systems are inspected, tested, and maintained in accordance with NFPA 25, Standard for the Inspection, Testing, and Maintaining of Water-based Fire Protection Systems. Records of system design, maintenance, inspection and testing are maintained in a secure location and readily available. 9.7.5, 9.7.7, 9.7.8, and NFPA 25

	Date sprinkler system last checked 						(annual)

	Who provided system test

	Water system supply source 						(K353)

	6. Portable Fire Extinguishers: Portable fire extinguishers are selected, installed, inspected, and maintained in accordance with NFPA 10, Standard for Portable Fire Extinguishers., 20.3.5.3, 21.3.5.3, 9.7.4.1, NFPA 10 (K355).

	Fire extinguishers shall be subject to maintenance at intervals of not more than 1 year, at the time of hydrostatic test, or when specifically indicated by an inspection or electronic notification. (NFPA 10, 7.3.1.1.1) Date of Last Maintenance:

	7. Smoking Regulations: Smoking regulations shall be adopted and shall include not less than the following provisions: 20.7.4, 21.7.4

	(1) Smoking shall be prohibited in any room, ward, or compartment where flammable liquids, combustible gases, or oxygen is used or stored and in any other hazardous location, and such area shall be posted with signs that read NO SMOKING or shall be posted with the international symbol for no smoking.

	(2) In health care occupancies where smoking is prohibited and signs are prominently placed at all major entrances, secondary signs with language that prohibits smoking shall not be required. (K741)

	8.* Electrical Systems – Essential Electric System Maintenance and Testing:

	The generator or other alternate power source and associated equipment is capable of supplying service within 10-seconds. If the 10-second criterion is not met during the monthly test, a process shall be provided to annually confirm this capability for the life safety and critical branches. Maintenance and testing of the generator and transfer switches are performed in accordance with NFPA 110.

	Generator sets are inspected weekly, exercised under load 30 minutes 12 times a year in 20-40 day intervals, and exercised once every 36 months for 4 continuous hours. Scheduled test under load conditions include a complete simulated cold start and automatic or manual transfer of all EES loads, and are conducted by competent personnel.

- Weekly inspections: fuel level, hoses, belts, oil level, cooling water level, radiator clear, battery electrolyte level, housekeeping of enclosure, and general visual inspection for damage.

- Monthly load tests meet NFPA 110 criteria. (See appendix A.8, 8.4.2, or 8.4.2.4 for natural gas.)

- If not meet monthly load tests, then annual load bank test. (See appendix A.8, 8.4.2.3)

- 36 month load bank test for 4 continuous hours. (See A.8, 8.4.9)

	Main and feeder circuit breakers are inspected annually, and a program for periodically exercising the components is established according to manufacturer requirements.

	Written records of maintenance and testing are maintained and readily available.

	EES electrical panels and circuits are marked and readily identifiable. (K918)

	9. Biomedical electrical inspection reports. Electrical Equipment – Testing and Maintenance Requirements: The physical integrity, resistance, leakage current, and touch current tests for fixed and portable patient-care related electrical equipment (PCREE) is performed as required in 10.3.

	Testing intervals are established with policies and protocols. All PCREE used in patient care rooms is tested in accordance with 10.3.5.4 or 10.3.6 before being put into service and after any repair or modification. Any system consisting of several electrical appliances demonstrates compliance with NFPA 99 as a complete system.

	Service manuals, instructions, and procedures provided by the manufacture include information as required by 10.5.3.1.1 and are considered in the development of a program for electrical equipment maintenance. Electrical equipment instructions and maintenance manuals are readily available, and safety labels and condensed operating instructions on the appliance are legible.

	A record of electrical equipment tests, repairs, and modifications is maintained for a period of time to demonstrate compliance in accordance with the facility's policy.

	Personnel responsible for the testing, maintenance and use of electrical appliances receive continuing trained. 10.3, 10.5.2.1, 10.5.2.1.2, 10.5.2.5, 10.5.3, 10.5.6, 10.5.8 (K921)

	10.* Receptacles and Line Isolation Monitors - Electrical Systems – Maintenance and Testing Hospital-grade receptacles at patient bed locations and where deep sedation or general anesthesia is administered, are tested after initial installation, replacement or servicing.

	Additional testing is performed at intervals defined by documented performance data. Receptacles not listed as hospital-grade at these locations are tested at intervals not exceeding 12 months. The facility shall establish a testing interval and maintain testing records. See appendix for testing criteria.

	Line isolation monitors (LIM), if installed, are tested at intervals of ≤ 1 month by actuating the LIM test switch per 6.3.2.6.3.6, which activates both visual and audible alarm. For, LIM circuits with automated self-testing, this manual test is performed at intervals ≤ 12 months. LIM circuits are tested per 6.3.3.3.2 after any repair or renovation to the electric distribution system.

	Records are maintained of required tests and associated repairs or modifications, containing date, room or area tested, and results. 6.3.4 (NFPA 99), (K914).

	11. Heating, Cooling, Ventilating, and Process Systems – serving spaces or providing health care functions covered by this code or listed within ASHRAE 170, Ventilation of Health Care Facilities, shall be provided in accordance with ASHRAE 170. (NFPA 99, 9.3.1). (K500)

	Final filters and filter frames should be visually inspected for pressure drop and for bypass monthly. Filters should be replaced based on pressure drop or maintenance schedule with filters that provide the efficiencies specified. (ASHRAE 170, Informative Appendix A, Operations and Maintenance Procedures.) A log of filter replacements should be maintained for each air handler.

	Records demonstrating that the RH was being monitored in anesthetizing locations and that they have taken timely corrective actions in instances when internal monitoring determines the RH levels are below the permitted range (20-60% RH). (ASHRAE 170, Table 7.1)

	12. Flame Spread Ratings: for following finishes (other than concrete, plaster, or gypsum board).  Note: All new finishes are those installed since July 5, 2016, i.e., the final rule effective date of CMS adoption.

	Interior Wall and Ceiling Finish: Interior wall and ceiling finishes in exits and exit access corridors shall have a flame spread rating of Class A or Class B. The reduction in class of interior finish for a sprinkler system as prescribed in 10.2.8.1 is permitted. All other areas may be class C rated material. Indicate flame spread rating(s) walls. _______________________________ 20.3.3, 21.3.3, 38.3.3, 39.3.3, 10.2 (K331)

	13.*	Inspection of Doors in Means of Egress - Records – General Aisles, passageways, corridors, exit discharges, exit locations, and accesses are in accordance with Chapter 7. Fire-rated door assemblies and certain other doors in the means of egress shall be tested annually or per an accepted performance-based evaluation schedule approved by the authority having jurisdiction, AHJ, per NFPA 80, 2010, Ch. 5.2. A written record of the inspections and testing shall be signed and kept for inspection by the AHJ. NFPA101, 7.2.1.15 See the appendix for more detail. (K200)

	14.	Features of Fire Protection – Fire Loss Prevention in Operating Room:

	Periodic evaluations (see next check box for schedule) are made of hazards that could be encountered during surgical procedures, and fire prevention procedures are established.

	Incidents are reviewed monthly, and procedures are reviewed annually. 15.13 (NFPA 99)

	When flammable germicides or antiseptics are employed during surgeries utilizing electrosurgery, cautery or lasers:

  - packaging is non-flammable

  - applicators are in unit doses

  - preoperative "time-out" is conducted prior the initiation of any surgical procedure to verify application site is dry prior to draping and use of surgical equipment of pooling of solution has not occurred or has been corrected

  - solution-soaked materials have been removed from the OR prior to draping and use of surgical devices

  - policies and procedures are established outlining safety precautions related to the use of flammable germicide or antiseptic use.

	Procedures are established for operating room emergencies including alarm activation, evacuation, equipment shutdown, and control operations. Emergency procedures include the control of chemical spills, and extinguishment of drapery, clothing and equipment fires.

	Training is provided to new OR personnel (including surgeons), continuing education is provided. (K933)

	15.* Risk Assessment: Building System Categories Building systems are designed to meet Category 1 through 4 requirements as detailed in NFPA 99. Categories are determined by a formal and documented risk assessment procedure performed by qualified personnel, see Chapter 4 (NFPA 99). The facility must define its risk assessment methodology, implement the methodology, and document the results in relation to the risk categories contained in the NFPA99 Health Care Facilities Code. No particular risk assessment procedure is required. The facility will determined the procedure that most meets their needs within the requirement of the NFPA code. For additional information see the appendix of NFPA 99, A4.1 and A4.2. (K901)

	Gas and Vacuum Piped Systems, Inspection and Testing Operations: The gas and vacuum systems are inspected and tested as part of a maintenance program and include the required elements. Records of the inspections and testing are maintained as required. 5.1.14.2.3, B.5.2, 5.2.13, 5.3.13, 5.3.13.4 (NFPA 99) (K908)

- Medical gas, vacuum, WAGD, or support gas systems have documented maintenance programs. The program includes an inventory of all source systems, control valves, alarms, manufactured assemblies, and outlets. Inspection and maintenance schedules are established through risk assessment considering manufacturer recommendations. Inspection procedures and testing methods are established through risk assessment. Persons maintaining systems are qualified as demonstrated by training and certification or credentialing to the requirements of ASSE 6030 or 6040. 5.1.14.2.1, 5.1.14.2.2, 5.1.15, 5.2.14, 5.3.13.4.2 (NFPA 99) (K907)

	Electrical Systems Wet Procedure Locations: Operating rooms are considered wet procedure locations, unless otherwise determined by a risk assessment conducted by the facility governing body. Operating rooms defined as wet locations are protected by either isolated power or ground-fault circuit interrupters. A written record of the risk assessment is maintained and available for inspection. 6.3.2.2.8.4, 6.3.2.2.8.7, 6.4.4.2. (K913).

	16.	Fire Marshal Reports: The facility shall supply a copy of the previous two years of Fire Marshal reports on the TDSHS form. (K9999)

Date of Last Inspection:

The following items, while not absolutely required will be helpful in expediting the LSC Survey:

	Provide overall floor plan(s) of the facility (8 ½ x 11” or 11” x 17”) showing room names or numbers.

	Date on which construction was completed, or on which plans were approved by Texas Department of State Health Services for construction.

	Copies of documents (from ASC’s files) resulting from most recent Life Safety Code Survey, “Form HCFA – 2567” , entitled “Summary of Deficiencies and Plans of Correction”.

Appendix AHCO

A.3. Four Core Requirements for Emergency Preparedness:

1)	Risk assessment and emergency planning for “all-hazards” for a specific location. These include, but are not limited to: equipment and power failure, interruption in communications, loss of part of a facility, and interruptions in water and food.

2)	Facilities must develop and implement policies and procedures that support the risks identified in the risk assessment.

3)	A communication plan must be established with state and local public health departments and emergency management agencies.

4)	Training and testing must be developed for new and existing staff in emergencies with annual refresher training. The facility must also conduct drills and exercises. (Federal Register, 81 FR 63859)

A.8. NFPA 110, 2010, Section 8.4: EES Operational Inspection and Testing:

The following section contains the NFPA 110 requirements for inspection and testing of the emergency electrical system, EES. Verify that these requirements are being followed by those responsible for testing.

8.4  Operational Inspection and Testing.

8.4.1* EPSSs, including all appurtenant components, shall be inspected weekly and exercised under load at least monthly. A.8.4.1  Weekly inspection does not require running of the EPS. Running unloaded generators as part of this weekly inspection can result in long-term problems such as wet stacking.

8.4.1.1  If the generator set is used for standby power or for peak load shaving, such use shall be recorded and shall be permitted to be substituted for scheduled operations and testing of the generator set, providing the same record as required by 8.3.4.

8.4.2* Diesel generator sets in service shall be exercised at least once monthly, for a minimum of 30 minutes, using one of the following methods:

(1)  Loading that maintains the minimum exhaust gas temperatures as recommended by the manufacturer (Note: see generator operation manual or call manufacturer)

(2)  Under operating temperature conditions ad at not less than 30 percent of the EPS nameplate kW rating (Note: kW rating will typically be stamped on name plate on generator)

Note: kW for a load test may be calculated as the (volts (480) x the average of the amps for the three phases x 1.732) divided by 1000 then multiplied by the power factor of 0.8.  This can be compared to the kW rating of the generator to determine the percent loading.

8.4.2.1  The date and time of day for required testing shall be decided by the owner, based on facility operations.

8.4.2.2  Equivalent loads used for testing shall be automatically replaced with the emergency loads in case of failure of the primary source. (Note: actual power outages may be used if they are of sufficient duration.)

8.4.2.3  Diesel-powered EPS installations that do not meet the requirements of 8.4.2 shall be exercised monthly with the available EPSS load and shall be exercised annually with supplemental loads at not less than 50 percent of the EPS nameplate kW rating for 30 continuous minutes and at not less than 75 percent of the EPS nameplate kW rating for 1 continuous hour for a total test duration of not less than 1.5 continuous hours. (Note: this has changed from older codes, and no longer requires 2 hours run time.)

8.4.2.4  Spark-ignited generator sets shall be exercised at least once a month with the available EPSS load for 30 minutes or until the water temperature and the oil pressure have stabilized. (Note: this is for natural gas generators and others fuel type where spark plugs are utilized.)

8.4.2.4.1  The date and time of day for required testing shall be decided by the owner, based on facility operations.

8.4.2.4.2  Equivalent loads used for testing shall be automatically replaced with the emergency loads in case of failure of the primary source. (Note: actual power outages may be used if they are of sufficient duration.)

8.4.3  The EPS test shall be initiated by simulating a power outage using the test switch(es) on the ATSs or by opening a normal breaker. Opening a normal breaker shall not be required.

8.4.4  Load tests of generator sets shall include complete cold starts.

8.4.5  Time delays shall be set as follows:

(1)  Time delay on start:

(a) 1 second minimum

(b) 0.5 second minimum for gas turbine units

(2)  Time delay on transfer to emergency: no minimum required

(3)  Time delay on restoration to normal: 5 minutes minimum

(4)  Time delay on shutdown: 5 minutes minimum

8.4.6  Transfer switches shall be operated monthly.

8.4.6.1  The monthly test of a transfer switch shall consist of electrically operating the transfer switch from the standard position to the alternate position and then a return to the standard position.

8.4.7* EPSS circuit breakers for Level 1 system usage, including main and feed breakers between the EPS and the transfer switch load terminals, shall be exercised annually with the EPS in the “off” position. A.8.4.7  Circuit breakers should be tested under simulated overload conditions every 2 years.

8.4.7.1  Circuit breakers rated in excess of 600 volts for Level 1 system usage shall be exercised every 6 months and shall be tested under simulated overload conditions every 2 years.

8.4.8  The routine maintenance and operational testing program shall be overseen by a properly instructed individual.

8.4.9* Level 1 EPSS shall be tested at least once within every 36 months. A.8.4.9  The intent of this requirement is to provide reasonable assurance that the EPSS with all of its auxiliary subsystems is capable of running for the duration of its assigned class with its running load. A full facility power outage is not intended for this test but is recommended where a total facility power outage has not occurred within the last 36 months. Supplemental load banks are not required. After the test, the fuel supply should be replenished if necessary.

8.4.9.1  Level 1 EPSS shall be tested continuously for the duration of its assigned class (see Section 4.2).

8.4.9.2  Where the assigned class is greater than 4 hours, it shall be permitted to terminate the test after 4 continuous hours.

8.4.9.3  The test shall be initiated by operating at least one transfer switch test function and then by operating the test function of all remaining ATSs, or initiated by opening all switches or breakers supplying normal power to all ATSs that are part of the EPSS being tested.

8.4.9.4  A power interruption to non-EPSS loads shall not be required.

8.4.9.5  The minimum load for this test shall be as specified in 8.4.9.5.1, 8.4.9.5.2, or 8.4.9.5.3.

8.4.9.5.1  For a diesel-powered EPS, loading shall be not less than 30 percent of the nameplate kW rating of the EPS. A supplemental load bank shall be permitted to be used to meet or exceed the 30 percent requirement. (Note: this is a change from older codes.)

8.4.9.5.2  For a diesel-powered EPS, loading shall be that which maintains the minimum exhaust gas temperatures as recommended by the manufacturer. (Note: 30% loading and minimum exhaust gas temperatures must both be achieved.)

8.4.9.5.3  For spark-ignited EPSs, loading shall be the available EPSS load.

8.4.9.6  The test required in 8.4.9 shall be permitted to be combined with one of the monthly tests required by 8.4.2 and one of the annual tests required by 8.4.2.3 as a single test.

8.4.9.7  Where the test required in 8.4.9 is combined with the annual load bank test, the first 3 hours shall be at not less than the minimum loading required by 8.4.9.5 and the remaining hour shall be at not less than 75 percent of the nameplate kW rating of the EPS.

“EPSS circuit breakers for Level 1 system usage, including main and feed breakers between the EPS and the transfer switch load terminals, shall be exercised annually with the EPS in the “off” position.” - NFPA 110, 2010, 8.4.7*. Note: “Circuit breakers should be tested under simulated overload conditions every 2 years.” - NFPA 110, 2010, A.8.4.7.  As an example, the simulated overload test may be done with a Megger Electric Science, Inc., MS-2A, Circuit Breaker and Overcurrent Relay Test Set.

A.10. Receptacles shall be tested for:

- The physical integrity of each receptacle shall be confirmed by visual inspection.

- The continuity of the grounding circuit in each electrical receptacle shall be verified.

- Correct polarity of the hot and neutral connections in each electrical receptacle shall be confirmed.

- The retention force of the grounding blade of each electrical receptacle (except locking-type receptacles) shall be not less than 115 g (4 oz). (NFPA 99, 6.3.3.2)

A.13. Inspection of Door Openings (NFPA 101, 7.2.1.15)

Door assemblies for testing and inspection shall include:

- Doors with panic hardware for fire exit hardware in accordance with 7.2.1.7.

- Doors in exit enclosures (doors connecting to exit passageways, 7.2.6.2).

- Electrically controlled egress doors

- Doors with special locking arrangements subject to 7.2.1.6. Such as delayed-egress locking systems, access- controlled egress door assemblies, and elevator lobby exit access door assemblies.

- All fire-rated door assemblies.

A.15. Risk Categories: The categories are based on the degree of harm from the worst-outcome scenario of failure and the reliability of the equipment expected to avoid harm.

Category 1: Systems in which failure is likely to cause major injury or death. Systems expected to work or be available at all times to support patient needs. Subjects are intended to be subjected to invasive procedures and connected to line–operated, patient care-related appliances such as ventilators or anesthetizing machines. Examples: include, but are not limited to, critical care such as intensive care, and special care treatment such as angiography, cardiac catherterization, delivery, invasive procedures, post-anesthesia care, emergency and other similar types of care.

Category 2: Systems in which failure is likely to cause minor injury to patients. Expected to provide a high level of reliability. However, limited short durations of equipment downtime can be tolerated without significant impact on patient care. These systems support patient needs but are not critical for life support (i.e. not serious or involving risk of life). Examples: General Care such as inpatient bedroom care, dialysis, in vitro fertilization, procedural, and similar care. Procedural care includes placement of peripheral intravenous needles or catheters, endoscopy, urethral catheters, and other similar procedures.

Category 3: Systems in which failure is not likely to cause injury, but can cause discomfort. Normal building system reliabilities are expected. Such systems support patient needs, but failure of such equipment would not immediately affect patient care. Such equipment is not critical for life support. Example: Basic Care such as examination and treatment procedures in clinics, medical and dental office care, and limited care facilities. Note: deep sedation and general anesthesia shall not be considered Category 3, and basic care shall not be required to be served by an EES.

Category 4: No impact on patient care and would not be noticeable to patients in the event of failure. Examples: Support rooms such as anesthesia work rooms, sterile supply, laboratories, morgues, waiting rooms, utility rooms, and lounges.

See A.4.1.1 in NFPA 99 for examples of major injury (NFPA 99).

See A4.2 in NFPA 99 for references on risk assessment procedures (NFPA 99)